## Sheet1
Current | 300 |  | Choose 5 from the pull down menu for amptector testing
Sensor
| In Setting | Ir / Test amps | MIN | MAX
LTPU | 0.5 | 150 | 156.75 | 173.25
LTD | 4 | 900 | 2.8 | 4
STPU | 4 | 600 | 570 | 630
STD | 0.3 | 900 | 0.276 | 0.3
STD * | 0.25 | 750 | 0.448 | 0.64
INST | 4 | 1200 | 1080 | 1320
GFPU | 0.25 | 75 | 67.5 | 82.5
GFD | 0.55 | 112.5 | 0.506 | 0.55
GFD* | 0.1 | 2.5 | 0.117 | 0.202
Fields in yellow have drop down selections.
Test values and Min/ Max values will automatically populate the appropriate fields.
New Magnum Test Kit does not support I2T settings.
ST FLAT | MIN | MAX |  | ST * | MIN | MAX |  | GF FLAT | MIN | MAX | GF * | MIN | MAX
0.1 | 0.06 | 0.13 |  | 0.1 | 0.192 | 0.332 |  | 0.1 | 0.06 | 0.13 | 0.1 | 0.117 | 0.202
0.15 | 0.1 | 0.17 |  | 0.15 | 0.288 | 0.46 |  | 0.15 | 0.1 | 0.17 | 0.15 | 0.175 | 0.28
0.2 | 0.15 | 0.22 |  | 0.2 | 0.384 | 0.563 |  | 0.2 | 0.15 | 0.22 | 0.2 | 0.234 | 0.343
0.25 | 0.23 | 0.25 |  | 0.25 | 0.448 | 0.64 |  | 0.25 | 0.23 | 0.25 | 0.25 | 0.27 | 0.39
0.3 | 0.276 | 0.3 |  | 0.3 | 0.537 | 0.768 |  | 0.3 | 0.276 | 0.3 | 0.3 | 0.327 | 0.46
0.35 | 0.322 | 0.35 |  | 0.35 | 0.627 | 0.896 |  | 0.35 | 0.322 | 0.35 | 0.35 | 0.382 | 0.546
0.4 | 0.368 | 0.4 |  | 0.4 | 0.716 | 1.024 |  | 0.4 | 0.368 | 0.4 | 0.4 | 0.436 | 0.624
0.45 | 0.414 | 0.45 |  | 0.45 | 0.806 | 1.152 |  | 0.45 | 0.414 | 0.45 | 0.45 | 0.491 | 0.702
0.5 | 0.46 | 0.5 |  | 0.5 | 0.896 | 1.28 |  | 0.5 | 0.46 | 0.5 | 0.5 | 0.546 | 0.78
[8 empty] | 0.55 | 0.506 | 0.55 | 0.6 | 0.655 | 0.936
[8 empty] | 0.6 | 0.552 | 0.6 | 0.65 | 0.709 | 1.014
[8 empty] | 0.65 | 0.598 | 0.65 | 0.7 | 0.764 | 1.092
[8 empty] | 0.7 | 0.644 | 0.7 | 0.75 | 0.819 | 1.17
[8 empty] | 0.75 | 0.69 | 0.75 | 0.8 | 0.873 | 1.248
[8 empty] | 0.8 | 0.736 | 0.8 | 0.85 | 0.928 | 1.326
[8 empty] | 0.85 | 0.782 | 0.85 | 0.9 | 0.982 | 1.404
[8 empty] | 0.9 | 0.828 | 0.9 | 0.95 | 1.037 | 1.482
[8 empty] | 0.95 | 0.874 | 0.95 | 1 | 1.092 | 1.56
[8 empty] | 1 | 0.92 | 1
LTPU SETTINGS | LTD SETTINGS | STPU SETTINGS | STD SETTINGS | STD * SETTINGS | INST SETTINGS | GFPU SETTINGS | GFD SETTINGS | GFD* SETTINGS
0.4 | 2 | 1.5 | 0.1 | 0.1 | 2 | 0.25 | 0.1 | 0.1 |  | Current Sensor Selection
0.45 | 2.5 | 2 | 0.15 | 0.15 | 2.5 | 0.3 | 0.15 | 0.15 |  | 5
0.5 | 3 | 2.5 | 0.2 | 0.2 | 3 | 0.35 | 0.2 | 0.2 |  | 200
0.55 | 3.5 | 3 | 0.25 | 0.25 | 3.5 | 0.4 | 0.25 | 0.25 |  | 250
0.6 | 4 | 3.5 | 0.3 | 0.3 | 4 | 0.45 | 0.3 | 0.3 |  | 300
0.65 | 4.5 | 4 | 0.35 | 0.35 | 4.5 | 0.5 | 0.35 | 0.35 |  | 400
0.7 | 5 | 4.5 | 0.4 | 0.4 | 5 | 0.55 | 0.4 | 0.4 |  | 600
0.75 | 5.5 | 5 | 0.45 | 0.45 | 5.5 | 0.6 | 0.45 | 0.45 |  | 630
0.8 | 6 | 5.5 | 0.5 | 0.5 | 6 | 0.65 | 0.5 | 0.5 |  | 800
0.85 | 6.5 | 6 |  |  | 6.5 | 0.7 | 0.55 | 0.55 |  | 1000
0.9 | 7 | 6.5 |  |  | 7 | 0.75 | 0.6 | 0.6 |  | 1200
0.95 | 7.5 | 7 |  |  | 7.5 | 0.8 | 0.65 | 0.65 |  | 1250
1 | 8 | 7.5 |  |  | 8 | 0.85 | 0.7 | 0.7 |  | 1600
| 8.5 | 8 |  |  | 8.5 | 0.9 | 0.75 | 0.75 |  | 2000
| 9 | 8.5 |  |  | 9 | 0.95 | 0.8 | 0.8 |  | 2500
| 9.5 | 9 |  |  | 9.5 | 1 | 0.85 | 0.85 |  | 3000
| 10 | 9.5 |  |  | 10 |  | 0.9 | 0.9 |  | 3200
| 10.5 | 10 |  |  |  |  | 0.95 | 0.95 |  | 4000
| 11 | [5 empty] | 1 | 1
11.5
12
12.5
13
13.5
14
14.5
15
15.5
16
16.5
17
17.5
18
18.5
19
19.5
20
20.5
21
21.5
22
22.5
23
23.5
24